This checklist is provided to allow building owners/representatives to correct deficiencies in their facilities prior to a Fire Department inspection.

Please contact the Lafayette Fire Prevention Bureau at (765) 807-1600 for assistance.

Exterior of Building

- The address shall be sized and located so that it is readily visible from the street (4-inch high minimum). The numbers must be in contrasting color to the building color.

- Exits from the building must be clear to an open area, not blocked by parking or vegetation.

- Grounds must be clear of debris.

- Gas meter must be protected (with bumpers) if in an area where it could be damaged.

- Is there a Knox-Box (fire department key box) on the building? If so, are the correct keys inside?

Occupant Load

All assembly occupancies must have their maximum occupant capacity reviewed by Fire Prevention Bureau personnel. Whenever the arrangement of the space(s) changes, the capacity must be reviewed again.

- Capacity signs must be displayed at the main entrance to each space. If the facility no longer has a sign or needs a replacement, please contact the Fire Prevention Bureau at 807-1600

Exit Doors / Door Hardware

- In places of Public Assembly or Educational occupancies with a capacity of 50 persons or more, there must be at least two approved exits and the doors must swing in the direction of egress.  The doors shall have approved panic hardware on all designated exit doors. Other locking devices are not allowed.

(EXCEPTION: In Group A having an occupant load of 300 or less, Groups B, F, M and S, and in places of religious worship, The main entry door is permitted to be equipped with a key operated locking device from the egress side provided that the locking device is readily distinguishable as locked and a readily visible durable sign is posted on the egress side or adjacent to the door stating: THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING IS OCCUPIED. The lettering on the sign shall be at least 1 inch high on a contrasting background.

- All doors designated as exits must have a minimum 32" clear width when fully open.

Aisles

- Aisles leading to an exit door shall have at least 44” of clear width.

- Aisles shall not be obstructed.

- Where tables and chairs are used, access shall be maintained to all aisles.

Exit Signage and Emergency Lighting

- All exits must be clearly indicated with an approved illuminated exit sign.

- To ensure continued illumination for at least 90 minutes, the exit signs and emergency lights must have a primary and a back-up power source in case of power loss. The back- up power source can be from storage batteries, an on-site generator, or the like.

- The entire exit path (including immediately outside the exit door) must be lighted at all times.

Fire Extinguishers

- If required, you must have the proper type of fire extinguishers. The size, type and location are determined by the hazards they are intended to protect.

- Insure all extinguishers are inspected, certified, and tagged annually by a qualified contractor.

- The contractor will advise you on the required size, type and location. You may look in the yellow pages or conduct a web search under Fire Extinguishers for a contractor.

- All fire extinguishers must be accessible and mounted with the bottom of the extinguisher a minimum of 4 inches off the floor and the handle a maximum of 60 inches above the floor.

Compressed Gas Cylinders

- All compressed gas cylinders in use or storage, (full or empty) shall be adequately secured to prevent falling or being knocked over. We encourage the use of chain(s) for this purpose. Rope and bungee cords have a stretch component and are subject to degradation by fire. The cylinders can also be nested together or in rack storage.

Storage

- Storage of combustible materials must be kept at least 24 inches from the ceiling and at least 3 feet from gas fired or heat producing appliances, e.g. furnace/water heater.  Combustible or flammable liquids not in retail-size containers are prohibited from being in a public assembly building unless properly stored in an approved flammable storage cabinet. This includes fuels contained in weed trimmers, lawn mowers, snow throwers etc.

Electrical

- A minimum open area of 30 inches in width, 36 inches in depth and 78 inches in height in front of an electrical circuit panel is required.

- Electrical panels must be installed according to the manufacturer’s recommendations and the listing of the panel.

- Panel must be mounted securely on the wall.

- Panel door must close and latch.

- All openings in panel must be covered.

- The main disconnect must be labeled.

- All junction boxes, switches, etc. must have cover plates installed.

- Extension cords may not be used in lieu of permanent wiring.

- All smoke detectors must be tested and installed properly

Life Safety Systems

Sprinkler System

- The sprinkler system (including standpipes or fire pump) must be tested, certified and tagged annually by a licensed contractor.

- The report must be on file and a copy forwarded to Lafayette Fire Prevention Bureau upon request.

- All system components must have proper signage so that the Fire Department can determine what part of the building is served by each component.

- All control valves must be accessible with a minimum 2 feet to the sides and 3 feet in front.

- All valves must be electronically supervised and/or chained in the open position.

- Spare sprinkler box must be provided with spare sprinklers and wrench.

- Fire department connection must have caps in place.

- Nothing may be attached to any part of the sprinkler system.

- All sprinkler heads must have a minimum vertical clearance of 18 inches from any decoration, display or storage.

Fire Alarm System

- The fire alarm system, must be tested, certified and tagged annually by a licensed contractor.

- The report must be on file and a copy forwarded to the Lafayette Fire Prevention Bureau upon request.

- All system components must be maintained and operate properly.

Commercial Cooking Operations

- All non-residential cooking operations regulated by the Health Department must be properly protected with a listed hood and suppression system.

- Deep fat fryers must have a 16 inch separation (horizontal or vertical) to open flames.

- The fire suppression system must be inspected and maintained every six months.

- The report must be on file and a copy forwarded to Lafayette Fire Prevention Bureau, upon request

- Remote Hand pull must be located properly, on the way out of the cooking area.

- All cooking equipment and components (hoods, ducts, filters, etc.) must be free of excessive grease accumulation.

- Kitchens utilizing deep fat or oil fryer(s) must have a “K” class, wet chemical extinguisher and placard specifically for the fryer(s)

- Relocating or changing of cooking appliances requires an evaluation by a qualified contractor

Emergency Generator

- The emergency generator (if present) must be tested and maintained properly. Weekly operation is required.

The generator test log must be on site.